## Design Stormwater
Appendix - A : Design Stormwater Flow Rate Calculation Sheet
Type of Section
1 | Rect. | :Rectangular
2 | Trape. | :Trapezoidal
3 | Trian | :Traingular
Design Flowrate Calculation Procedure:
1 | Calculate Catchament Area from each catch basin and find equivalent area after multiplying with runoff coefficent
2 | Select pipe diameter, slope for given cross section.
3 | Calculate Time of Concentration for each Pipe separatly.
4 | Tc = T intial + T pipe
5 | T initial =
6 | Calculate Design Flow Rate for Each Pipe = Cummulative Peak Flow Rate
7 | For Tie-in apart from Toilet Blocks Assume Flow Rate = 5m3/hr for Design Purpose
Note: Copy Colum A,B,C,J to Appendix A
| Sr. No. | From Node | To Node | Length of Pipe | Slope (Gradient) | Drop | Manning coeff | Catchment Area (CA) | [5 empty] | Time of Concentration (TC = Tinitial + TFlow) |  |  |  |  | Design Flow |  | Channel Conveyance Factor |  |  | Channel Size |  |  | Channel Hydraulic Properties | [5 empty] | Check
[8 empty] | Asphalt | Runoff Coef. | Marl/ Unpaved | Runoff Coef. | Equiv. Area | Cumm. Area | Overland Flow | Channel Time | Cumm. Channel Flow Time | Time of Concentration | Rainfall Intensity | [5 empty] | Wetted Depth | Eco. Bottom Width | Provided Bottom Width | Wetted Area | Wetted Perimeter | Hydraulic Radius | Actaul Velocity | Actaul Discharge | Actaul Discharge
|  |  |  | L | 1:S | d | n | [6 empty] | Tinitial | Tflow | Tflow | TC | I = k/(t+b) | Q Design |  | Q*n/ S^0.5 | =(B.y)*((b*y)/(b+(2*y)) | y normal | y | b = 2y | b | A = b*y | P = b + 2y | R = A/P |  |  |  | Q Check | V Check | Overland Flow Time T (initial) = | = 2.53 min | Therefore use 10min
|  |  |  | m | m | m |  | m2 | C | m2 | C | m2 | m2 | min | min | min | min | mm/hr | m3/hr | m3/sec |  |  | m | m | m | m | m2 | m | m3/sec
| Zone-A | [33 empty] | Pipe Flow Time Tf(pipe) = Length / Velocity | Rainfall Intensity
| 1 | CS-71 | CS-72 | 10 | 100 | 0.1 | 0.015 | 772.187 | 0.9 | 0 | 0.6 | 694.9683 | 694.9683 | 10 |  |  | 10 | 65.1467 | 45.2749 | 0.012576 | 0.0018865 | 0.0013586 | 0.060447 | 0.060447 | 0.12089 | 0.2 | 0.0073078 | 0.24179 | 0.030224 | 0.64685 | 0.0047271 | 17.0174 | UNSAFE | #REF!
| 2 | CS-72 | CS-73 | 25 | 240 | 0.10417 | 0.015 | 2658.426 | 0.9 | 0 | 0.6 | 2392.5834 | 3087.5517 |  | 0.25766 | 0.25766 | 10.2577 | 64.7021 | 199.7711 | 0.055492 | 0.012895 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.69494 | 0.023846 | 85.8474 | #REF! | #REF! | Minimum Tc for system design = 10min | Where, | K = 2443 | b = 27.5
| 3 | CS-73 | CS-74 | 22 | 200 | 0.11 | 0.015 | 0 | 0.9 | 0 | 0.6 | 0 | 3087.5517 |  | 0.59957 | 0.85723 | 11.1149 | 63.2658 | 195.3363 | 0.05426 | 0.01151 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.76127 | 0.026123 | 94.0411 | #REF! | #REF! |  | For 5yr Storm Frequency
| 4 | CS-79 | CS-78 | 36 | 240 | 0.15 | 0.015 | 0 | 0.9 | 0 | 0.6 | 0 | 3087.5517 | 10 |  |  | 11.1149 | 63.2658 | 195.3363 | 0.05426 | 0.012609 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.69494 | 0.023846 | 85.8474 | #REF! | #REF!
| 4 | CS-77 | CS-76 | 36 | 240 | 0.15 | 0.015 | 0 | 0.9 | 0 | 0.6 | 0 | 3087.5517 |  | 0.86338 | 0.86338 | 11.9783 | 61.8821 | 191.0643 | 0.053073 | 0.012333 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.69494 | 0.023846 | 85.8474 | #REF! | #REF!
| 4 | CS-76 | CS-75 | 36 | 240 | 0.15 | 0.015 | 0 | 0.9 | 0 | 0.6 | 0 | 3087.5517 |  | 0.86338 | 1.7268 | 13.705 | 59.2889 | 183.0574 | 0.050849 | 0.011816 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.69494 | 0.023846 | 85.8474 | #REF! | #REF!
| 4 | CS-75 | CS-74 | 36 | 240 | 0.15 | 0.015 | 232 | 0.9 | 232 | 0.6 | 348 | 3435.5517 |  | 0.86338 | 2.5902 | 16.2952 | 55.7824 | 191.6433 | 0.053234 | 0.012371 | 0.0055414 | 0.11438 | 0.11438 | 0.22876 | 0.3 | 0.034314 | 0.52876 | 0.064896 | 0.69494 | 0.023846 | 85.8474 | #REF! | #REF!
I=K/((t+b))